## Slide 1
          Marco Schiaffino - Design INAF-ORA Radiotelescopio Croce del Nord
          Email : m.schiaffino@ira.inaf.it
AAVS1/LFAA RACK INTEGRATION
          Richard Bennett - Thermal Analysis
          UK Astronomy Technology Centre Science and Technology Facilities Council
          Email : richard.bennett@stfc.ac.uk

## Slide 2: RACK – AAVS1 Vs LFAA AAVS1 and LFAA rack comparison
 | AAVS1 | LFAA
N° OF SIDES WITH COMPONENTS | 1 | 2
N° OF SUBRACK/RACK | 2 | 8
N° OF TPM BOARDS/SUBRACK | 4 | 8
N° OF TPM BOARDS/RACK | 8 | 64
COOLING SYSTEM | AIR | HYBRID
N° OF POLARIZATIONS | 256 | 2048

## Slide 3: AAVS1 rack
Allocation of space:
6U - power supply (not included in the drawing)
1U - optical box
1U - supplier 10MHz / pps
1U - 1Gb switch
3U - deflector
1U - drawer 6 ventilation fans
6U - subrack TPM
1U - drawer 6 ventilation fans
3U - empty
1U - 40Gb switch
1U - optical box
1U - supplier 10MHz / pps
1U - 1Gb switch
3U - deflector
1U - drawer 6 ventilation fans
6U - subrack TPM
1U - drawer 6 ventilation fans
4U - empty
Total Height: 42U

## Slide 4: TPM ADU board hardware and thermal model
In the thermal model 90% of components are filtered out by size – can compensate by assigning surface roughness to the pcb

## Slide 5: AAVS1 sub-rack heat-sink preliminary test
T MAX (1): 57,3° C
T MAX (2): 56,9° C
T MAX (3): 58,5° C
T MAX (4): 58,4° C

## Slide 6: AAVS1 TPM sub-rack thermal model

## Slide 7: AAVS1 simulation – air velocity (on plane through front row of fans)

## Slide 8: AAVS1 simulation temperatures on ADU

## Slide 9: AAVS1 simulation heat source temperatures

## Slide 10: AAVS1 simulation ADU board temperatures
Board temperatures
analysis (4 TPM present):
56.4°C, 56.4°C, 56.4°C, 56.4°C
measured (one by one):
57.3°C, 56.9°C, 58.5°C, 58.4°C
Agreement between simulation and measurement appears to be good….
but could be serendipity…
Quickly converges for values of temperature, velocity and pressure at monitoring points but solution residuals are higher than one would like.
Ideally one would:
Re-mesh the model with coarser and finer mesh to check that the results are independent of the mesh
Re-run with different turbulence models

## Slide 11: AAVS1 rack thermal model

## Slide 12: AAVS1 rack thermal model mesh work in progress

## Slide 13: LFAA sub-rack concept heat pipes + water cooling
Management
board
Custom 7U height, depth 475 + manifolds
(8U would be better, to have an easier integration and larger contact surfaces)
TPM boards

## Slide 14: LFAA TPM concept heat pipes + water cooling
Existing TPM geometry with heat pipes to cool ADC and FPGA
The heat pipes are screwed directly to a water cooled block at the top or the bottom, the contact resistance and the film temperature difference must be determined. For 25W, 40mm of φ6mm tube and 0.025kg/sec water flow ΔTfilm = 7K.

## Slide 15: LFAA TPM sub-rack concept water cooling connections
Cold water input
Hot water output
Cold water input
Hot water output

## Slide 16: LFAA TPM sub-rack Concept connection of management and backplane
Management Board
Backplane Board
TPM Board (only one is visible)

## Slide 17: LFAA TPM sub-rack concept metal plate + water cooling
Custom 7U height, depth 475 + manifolds
TPM module
Management
board
TPM boards
Custom metal plate (aluminium or copper)
For 5mm thick copper ΔT along plate = 31K

## Slide 18: LFAA TPM sub-rack concept metal plate + water cooling
Cold water
input
Hot water
output
Cold water
input
Hot water output
Management Board
Backplane Board
TPM Board (only one is visible)

## Slide 19: LFAA TPM sub-rack concept metal plate + water cooling
Custom cold plates
Compression blocks (for the «metal plate» - «cold plate» contact)

## Slide 20: LFAA TPM sub-rack Concept Potential increase in the number of TPM boards
AAVS1 TPM module (21 hp)
Example of LFAA TPM module (10 hp)
4 TPM modules in each Sub-racks
128 RF Chains in each Sub-racks
Using the same concept of boards assembly – sandwich mode
8 TPM modules + 1 management board
In each Sub-rack
256 RF Chains in each Sub-rack

## Slide 21: LFAA TPM sub-rack Concept Potential increase in the number of TPM boards
AAVS1 TPM module (21 hp)
Example of LFAA TPM module (7 hp)
4 TPM modules in each Sub-rack
128 RF Chains in each Sub-rack
12 TPM modules (or 11 + 1 management board) in each Sub-rack
384 (352) RF Chains in each Sub-rack
Putting 32 RF chains in a single preADU board